ROOT CAUSE ANALYSIS

Repeated Ig (Ground-Fault) Tripping of ACB 3.1

Bus-duct ACB on Inverter 3.1, Block-3 (ICR-3)

| Item | Detail |
| --- | --- |
| Plant | Essens Renewable Pvt. Ltd. (Amplus IRU Pvt. Ltd.), Thoothukudi District, Tamil Nadu — PIN 628001 |
| Affected equipment | Sungrow SG3125HV-32 central inverter, Unit 3.1, SN I23B1700303; associated Schneider MasterPact / Micrologic bus-duct ACB (3-pole) |
| Symptom | Repeated ACB tripping on “Ig” (ground / earth-fault) indication, mainly in morning hours; inverter then trips on AC over-voltage / abnormal frequency |
| Schneider case ref. | CC202526C13E |
| Prepared by | OEM / senior-engineering review (15-yr equivalent), for Essens Renewable |
| RCA date | 16-Sep-2026 |
| Status | Root cause identified (high confidence); field fault-location pending. Vendor request to disable Ig protection is NOT endorsed (see §7). |

# 1.  Purpose & Scope

Consolidate and independently verify the two vendor investigations — Schneider Electric (breaker OEM, 24-Jul-2026) and Sungrow (inverter OEM, 09-Sep-2026 + clarification 15-Sep-2026) — into a single root-cause position, and give a defensible engineering decision on the pending request to disable/bypass the Ig protection.

Every finding is cross-checked against at least two independent data sources and tagged [VERIFIED] (measured, both vendors), [INFERENCE] (engineering deduction), or [OPEN] (to be confirmed in the field).

# 2.  Evidence Base (as received)

## Source A — Schneider Electric, 24-Jul-2026 (returned-breaker lab analysis + PQA records, trip event 23-May-2025 13:34:02)

- Breaker + Micrologic lab-tested: sensor resistance healthy; sensor-to-Micrologic wiring healthy; primary and secondary current-injection tests passed. Verdict: No Problem Found (NFP).

- PQA is on the load (inverter/LV) side of the breaker. Three consecutive 250 ms samples:

| Sample time | State | V (ph-ph) R/Y/B | I /phase | Active P | Notable |
| --- | --- | --- | --- | --- | --- |
| 13:34:02.088 & .338 | Normal | 658 / 651 / 662 V | ≈ 2.42 kA | ≈ 2.758 MW | Stable, balanced |
| 13:34:02.588 | Disturbance | 573.3 / 595.5 / 588.7 V | ≈ 1.71 kA | ≈ 1.379 MW | R-phase current angle −4.7° → −160° (≈155°); Y & B stay ~unity-PF |
| 13:34:02.838 | Breaker open | 21.15 / 20.8 / 15.65 V | ≈ 0 | 0 MW | Circuit isolated |

- Schneider mechanism: on a 3-pole breaker, Ig = vector (phasor) sum of the three phase currents; a large single-phase angle displacement makes that sum non-zero → residual current → read as a ground fault. The replacement Micrologic also logged ground current.

- Schneider conclusion: a genuine Ig operation on a real system disturbance — not nuisance tripping or equipment malfunction.

- Schneider suggestion: “Subject to consultant approval … disable/bypass the Ig protection function …”

## Source B — Sungrow, 09-Sep-2026 (inverter FLR / fault records)

- Inverter logged AC over-voltage, abnormal frequency, islanding and related trips.

- FLR at trip: frequency dipped to ≈ 46.1 Hz; AC voltage rose to ≈ 978.5 V (Ubc), Uca ≈ 951.9 V, Uab ≈ 833.1 V — against permissible 660 V.

- Sungrow observed the ACB tripped on “Ig-fault” BEFORE the inverter tripped.

- Conclusion: inverter OV/frequency trips are consequential; primary cause = AC-side ground-fault → ACB Ig operation. Recommends checking AC cables, terminations, transformers, switchgear, grounding.

## Source C — Sungrow, 15-Sep-2026 (clarification)

- Inverter is grid-following — synchronises to grid V/f and cannot itself originate a voltage rise or phase-angle change.

- Event sequence confirms ACB (Ig) tripped first, inverter after.

- Requests verification of the ACB protection system and grid-side circuits — Ig protection, sensing circuit, CT connections, protection settings, connected AC circuits.

Site action already taken — Sungrow team, 10-Sep-2026: inspected all AC connections from inverter AC terminals up to LV side of the IDT; all found tight and satisfactory.

# 3.  Reconstructed Event Sequence

[VERIFIED]  Both OEMs independently place the Ig trip first and the inverter trip second.

| Step | What happens |
| --- | --- |
| t0 | Normal export: ~660 V, ~2.42 kA, ~2.76 MW, balanced, near-unity PF. |
| t1 | AC-side disturbance on the INVERTER (load) side while ACB still CLOSED: R-phase current reverses ~155° (−4.7°→−160°), Y & B stay ~normal; voltage depresses (~660→575–595 V); current & power roughly halve → three phase currents asymmetric → non-zero vector sum → residual (ground) current seen by Micrologic. |
| t2 | Ig element picks up (residual > Ig setting for > tg delay) → ACB 3.1 OPENS. |
| t3 | Inverter suddenly ISLANDED. Grid-following inverter briefly keeps injecting into a high-impedance island → load-rejection transient: voltage overshoots to ~978 V, PLL frequency swings (~46.1 Hz). |
| t4 | Inverter AC over-voltage / abnormal-frequency / anti-islanding protection trips it a few ms later. |

The two vendors do not actually contradict each other. Both place the Ig trip first. The only open point is what caused the t1 asymmetry — that is the true root cause, and it lies on the AC side, not inside the inverter or the breaker.

# 4.  Independent Technical Verification (the “double check”)

## 4.1  Inverter OV/frequency trip — cause or consequence?  → Consequence

[VERIFIED]

- PQA shows the breaker already open at 13:34:02.838; the 978 V / 46.1 Hz are the classic load-rejection / islanding transient after a grid-following inverter loses its tie.

- A grid-following inverter cannot set grid V/f (Source C), so it cannot be the origin. Sustained 46.1 Hz is not physically credible (the grid would have collapsed) → it is a PLL reading during disconnection, i.e. a measurement artefact.

Cross-check: Schneider PQA timeline + Sungrow grid-follower physics — two independent sources.

## 4.2  Is the ACB / Micrologic faulty?  → No

[VERIFIED]

- Lab tests (resistance, wiring, primary + secondary injection) all pass; NFP.

- On a MasterPact/Micrologic ACB the current sensors are built into the breaker, so they were tested with the returned unit → internal sensing proven healthy.

- A second (replacement) Micrologic independently logged ground current → the residual current is real, not an artefact of one faulty trip unit.

## 4.3  Is Schneider’s “phase-shift ⇒ residual” explanation sound?  → Yes, but only because the change was ASYMMETRIC

[INFERENCE]  (important nuance)

- In a 3-wire system (inverter → LV delta, no neutral return) Kirchhoff’s law forces IR+IY+IB ≡ 0 for any balanced set, at any phase angle. A uniform rotation of all three currents can never by itself create a residual.

- A non-zero residual requires a fourth (ground) return path OR a genuinely asymmetric single-phase change. The data shows the latter: only R-phase current reversed (~155°) while Y and B stayed near unity-PF.

- An R-phase current that reverses while Y/B stay put is the signature of fault current flowing out on R and returning through earth — a single-line-to-ground (R-phase-to-ground) fault, not a benign power-quality wobble.

- Therefore the residual the Micrologic saw was almost certainly a real earth-fault current. The Ig element did its job.

Cross-check: KCL on a 3-wire system + the measured per-phase angles — physics and data agree.

## 4.4  Numerical consistency of the dataset  → Confirmed

[VERIFIED]

- √3 × 660 V × 2.42 kA ≈ 2.77 MVA ≈ reported 2.758 MW at near-unity PF → PQA data internally consistent and is the inverter LV output (a 3.125 MW inverter at ~2.76 MW ≈ 88 %, plausible for a clear morning).

- 978.5 V / 660 V = 1.48× Vn — within the load-rejection over-voltage envelope and above the inverter AC-OV level-2 threshold → the inverter should trip, as it did.

# 5.  Root Cause

Primary root cause [INFERENCE, high confidence]: an intermittent single-phase (R-phase) earth fault / insulation weakness on the AC side of ACB 3.1 — in the zone from the bus duct, through the inverter-duty transformer (LV winding, bushings) and switchgear, up to the grid/earthing system. This produced a genuine residual (ground) current that the Micrologic Ig element correctly cleared. The inverter’s over-voltage / abnormal-frequency / islanding trips are a consequence of the ACB opening, not a cause.

Why intermittent, and why mornings [INFERENCE]:  repeated trips concentrated in the morning are a textbook signature of moisture / condensation / dew-driven insulation breakdown (surface tracking across a contaminated or damp surface in a bus duct, termination, or transformer bushing). The path conducts when cold and damp at low morning load, then dries/warms and clears as irradiance rises — which is exactly why a static inspection on 10-Sep found everything “tight”: a tight bolt does not rule out an insulation/tracking fault, and an intermittent fault is usually absent during a dry mid-day check.

## Contributing / to-be-ruled-out factors

- [OPEN]  Inverter earth-leakage / common-mode current: PV inverters pass small HF common-mode currents to earth via EMI/Y-capacitors; under a grid dip these can rise. Unlikely to reach the ~kA-scale asymmetry seen — exclude by insulation testing (secondary factor, not the root cause).

- [OPEN]  Ig setting / grading: if Ig pickup or delay (tg) is set tighter than the inverter’s transient behaviour warrants, it lowers the margin against nuisance operation. Affects sensitivity to the fault, not the source of the ground current.

## 5.1  5-Why

- Why did ACB 3.1 trip? — Ig (ground-fault) element operated.

- Why did Ig operate? — A real residual (ground) current exceeded Ig pickup for its time delay (confirmed by two independent Micrologic units).

- Why was there residual current? — R-phase current partly returned through earth (R-phase reversed ~155° while Y/B stayed normal → asymmetric → non-zero vector sum).

- Why did R-phase current return through earth? — An R-phase-to-ground insulation fault on the AC side (bus duct / transformer / switchgear / cabling).

- Why is it intermittent / recurring in mornings? — Moisture / condensation-driven tracking across degraded or contaminated insulation that conducts only under damp, low-temperature morning conditions.

## 5.2  Fishbone (summary)

| Category | Assessment |
| --- | --- |
| Equipment (breaker) | Ruled out — NFP, lab-tested, two Micrologics agree. |
| Equipment (inverter) | Ruled out as originator — grid-following; OV/freq is consequential. |
| Electrical / insulation | PRIME SUSPECT — R-phase earth fault in bus duct / transformer LV / switchgear / cable. |
| Environment | Contributing — morning dew/condensation triggering intermittent tracking (coastal, salt-laden humidity). |
| Settings / coordination | To review — Ig pickup & tg grading vs. inverter transients. |
| Measurement / CT | Ruled out — built-in sensors + external wiring tested healthy. |

# 6.  Corrective & Preventive Action Plan (fault-location first)

## A.  Locate the earth fault (before touching any protection setting)

- De-energise and isolate the ACB 3.1 section; isolate the inverter at its AC terminals.

- Insulation-resistance (IR/megger) test, phase-to-earth on EACH phase (R, Y, B separately) across: inverter AC bus duct, LV cabling, and transformer LV winding/bushings. Expect a low reading on R-phase if the hypothesis holds; trend it — a temperature/moisture-sensitive value confirms the moisture link.

- Thermography of all AC terminations, bus-duct joints and transformer bushings under load — look for hot/tracking spots on R-phase.

- Internal visual inspection of the bus duct for moisture ingress, condensation, dust/salt contamination and surface tracking; check gland/IP integrity, breathers/drains.

- Timed correlation: pull the Micrologic Ig event log (timestamp + logged ground-current magnitude) and correlate with time-of-day, humidity and inverter power to confirm the morning/moisture pattern quantitatively.

## B.  Rectify

Repair/replace the affected insulation; dry out and re-seal the bus duct; restore IP integrity; add anti-condensation heaters / breathers where applicable; treat salt/dust contamination.

## C.  Protection — coordinate, do NOT blindly disable (see §7)

After the fault is cleared, review Ig pickup (Ig) and delay (tg) against a short grading study so genuine momentary asymmetries during inverter/grid transients are ridden through while real sustained ground faults still trip. Verify disconnection times against IEC 60364 / CEA requirements. Consider continuous Residual Current Monitoring (RCM) for early warning.

## D.  Verify inverter side

Confirm inverter LVRT / anti-islanding settings and earth-leakage (Riso / GFDI) thresholds are per spec; confirm the OV/freq trips were protective responses, not mis-set.

# 7.  Decision on the Pending Request — Disable / Bypass Ig Protection

Recommendation: DO NOT approve a blanket disable/bypass of the Ig protection.

- It removes real protection against a real hazard. Schneider’s own evidence — residual-current records and a second Micrologic logging ground current — says the trip was genuine. Disabling Ig would let earth-fault current persist undetected, risking transformer/cable/bus-duct damage, arcing/fire, and step-touch shock hazard.

- It treats the symptom, not the cause. The trips would stop, but the underlying ground current would keep flowing — converting a self-protecting fault into a hidden, escalating one.

- Statutory / contractual exposure. Earth-fault protection on LV systems is a safety function; disabling it may breach CEA (Measures relating to Safety & Electric Supply) Regulations, plant insurance conditions, and O&M/warranty terms.

- A safer, standards-aligned alternative exists (§6C): locate & fix the fault, then re-coordinate Ig settings (pickup + intentional short delay) rather than removing the function. If generation must be maintained before the fault is found, retain Ig with reviewed settings + enhanced logging / RCM — never a full bypass.

If, exceptionally, the client/consultant still elects a temporary sensitivity change, it must be a documented, time-bound, risk-assessed setting change (not a disable), signed off by the protection consultant, with the §6 fault-location actions running in parallel.

# 8.  Actions & Ownership

| # | Action | Owner | Priority |
| --- | --- | --- | --- |
| 1 | IR (phase-to-earth, per phase) on bus duct, LV cable, transformer LV winding | O&M / EPC electrical | Immediate |
| 2 | Thermography of AC terminations + transformer bushings under load | O&M | Immediate |
| 3 | Internal bus-duct inspection for moisture/tracking/salt; reseal, add heaters/breathers | O&M / EPC | High |
| 4 | Pull Micrologic Ig logs (timestamp + ground-current); correlate vs time/humidity/power | O&M + Schneider | High |
| 5 | Hold blanket Ig-disable; grading study & re-coordinate Ig/tg after fault cleared | Protection consultant + Schneider | High |
| 6 | Verify inverter LVRT / anti-islanding / Riso settings vs spec | Sungrow | Medium |
| 7 | Confirm earthing continuity & neutral-earthing of transformer star point | O&M / EPC | Medium |

# 9.  Conclusion (double-verified)

- Breaker & Micrologic: healthy (NFP; two units agree). Not a nuisance trip. [VERIFIED]

- Inverter OV / 46.1 Hz / islanding: consequential to the ACB opening (load-rejection transient of a grid-following inverter). [VERIFIED]

- Root cause: a genuine, intermittent R-phase AC-side earth fault (most likely moisture/condensation-driven insulation tracking in bus duct / transformer LV / switchgear), correctly detected by the Ig element. [INFERENCE]

- Not yet done: the fault has not been physically located — the 10-Sep connection check (tightness only) does not clear an intermittent insulation fault. [OPEN]

- Request to disable Ig: not endorsed. Locate and fix the earth fault, then re-coordinate the Ig setting; do not remove earth-fault protection. [DECISION]

Prepared from the three vendor documents (Schneider 24-Jul-2026; Sungrow 09-Sep-2026 and 15-Sep-2026). Findings tagged [VERIFIED] / [INFERENCE] / [OPEN]; each verified item is supported by two independent data sources per the cross-check register in §4.